

Model Trio1000P

Owner Operation and

# Maintenance Manual

Field Controls

2630 Airport Road

Kinston, NC 28504

(252) 522-3031

**IMPORTANT SAFETY INSTRUCTIONS**

Read and save these instructions.

Always unplug the Trio-1000P Portable Air Purification System when it is not in operation, while the Filters or UVC germicidal lamps are being changed, and when cleaning. After servicing this equipment, both the front and top grill assemblies must be reinstalled in exactly the same manner as prior to removal. If either grill is not reinstalled properly, the Trio-1000P Portable Air Purification System will not turn on. This is a built in safety feature.

Before using the Trio-1000P Portable Air Purification System, extend the power cord and inspect for any signs of damage. Do not use the product if the power cord has been damaged.

Warning – This appliance is designed to be used on a flat level surface, and may not work properly on an uneven surface. To reduce the risk of electric shock and injury, do not place in a window. Always place the air purifier at least 12 inches (30.48 centimeters) away from heat sources such as stoves, radiators, or heaters.

Do not move the Trio-1000P Portable Air Purification System while it is in operation. Always unplug prior to moving.

Do not immerse the Portable Air Purification System in water, as permanent damage will occur. Refer to the “Performing Maintenance” section in this owner operation and maintenance manual.

**Field Controls Trio-1000P PORTABLE CATALYTIC AIR PURIFICATION SYSTEM FEATURES**

Thank you for purchasing a Trio-1000P Portable Air Purification System by Field Controls.

The Portable Air Purification System embodies unique air-purification technologies not found in any other air purifier. The PRO-Cell™ patented catalytic technology signifi-cantly reduces the presence of irritable and toxic airborne gaseous contaminants produced by common household cleaners and materials.

* A quiet, energy-efficient backward-curved impeller that moves 265 cubic feet of air per minute.
* An advanced electronic control system that monitors air quality, air flow and volume, filter and UVC germicidal lamp replacement time.
* A five-stage filtration system with gas-absorption media that absorbs toxic gas, organic hydrocarbons, exhaust fumes, formaldehyde, cleaning chemicals, low level ozone, unpleasant odors, and paint solvents.
* A hospital-grade three-stage HEPA filter removes allergens such as pollen, mold fungal spores, tobacco smoke, insecticide dust, dust mites, and particles down to 0.3 microns (0.00003 inch).
* The PRO-Cell™ photo-catalytic oxidation chamber reduces the spread of airborne disease in the home environment. The powerful UVC germicidal light has 150 times the ultraviolet intensity of bright sunlight, which kills viruses and bacteria on contact.
* Oxygen in the air, combined with photo-catalytic technology and UVC germicidal ultraviolet light, oxidizes airborne impurities too small to be filtered out.

The PRO-Cell™ photo-catalytic oxidation technology, which has received six patents from the USPTO, will keep the air clean and fresh in exactly the same way sunlight and oxygen clean the air we breathe in the outdoor environment.

**INSTALLING THE Field Controls Trio-1000P PORTABLE AIR PURIFICATION SYSTEM**

CAUTION This product is for indoor use only.


Before unpacking the product, inspect the shipping container for visible damage. If you feel that you may have received the product in a damaged condition, notify the shipper or supplier before opening the container. Remove the product from the box and inspect it for damage.

**Handle it carefully. Do not drop!**

Place the Purifier in a location that will not restrict air flow through either the air inlet or the air outlet, then plug in the electrical cord at the nearest electrical wall outlet.

**NOTE:** **The Trio-1000P Portable Air Purification System will perform a diagnostic test of indicator lights and functions when plugged in to the wall outlet. This will only happen once, unless the system is unplugged from the wall and reinstalled.**

**FIGURE 1**

**!**

1. **Press in Power (ON/OFF) button** to turn on the Purifier. Lights on the control panel **(figure 1**) will turn on and the UVC germicidal ultraviolet lamp will be on.
2. Look into the air outlet at the top of the **Trio-1000P** Air Purification System and confirm that the UVC germicidal ultraviolet lamp is on. You will see a faint blue glow when the lamp is on.

When the UVC germicidal ultraviolet lamp is on, the product is ready for operation.

**NOTE**: The “Air Quality” LED light may turn **red** on startup until the surrounding air quality improves.

When the air quality LED is **red**, the air flow is automatically in- creased by (2) power levels. The lowest fan speed cannot be reached until the air quality light turns **orange** in color, and then **green** as air quality reaches a safe level.

1. **Setting the fan speed and air volume to the correct room size.**

Press the ”**Fan Speed Button**” (**figure 1**) until the **green LED bar light** underneath ”Room Size/Fan

Speed” reaches the corresponding size of your room. Calculations in both ”square feet” and ”square meters” (length x width) measurements are conveniently listed at either side of the **green LED bar lights**. Correctly setting this indicator will keep the air volume at an optimum level.

1. Press the ”**Sleep Mode Button**” (**figure 1**) at night if you desire to reduce fan noise.

A **green** LED light will illuminate to the right side of the button. This will maintain constant airflow through the purifier and reduce fan speed to a minimum. Since there is no movement in the room, purification requirements are greatly reduced.

Press the Sleep Mode Button again to return to the normal air flow mode.

**Monitoring Operation**

You can always monitor the air quality of the room.

Air quality is sensed in real time by the chemical-detection sensor (see figure 1) which continually evaluates air quality. Air quality is expressed by one of (3) colors on the air quality LED light.

1. Green indicates good air quality.
2. Orange indicates poor air quality.
3. Red indicates bad air quality.

Air volume is automatically increased by (2) fan speed levels when the air quality indicator turns **red,** and will reset to a preset fan speed when the air quality indicator turns orange and then green.

It is normal for the air quality indicator to temporarily be **red** during periods of house cleaning,  painting, or cooking meals.

**MAINTENANCE OF Trio-1000P Portable Air Purification System**

You should also keep an eye on the Service Panel which tells you when maintenance will soon be  required.

**What the Service Panel Indicator Lights Mean (“Air Filter” and “UV Lamp”)**

Indicator lights on the Service Panel tell you if either the air filters or the germicidal ultraviolet lamp will soon need to be cleaned or replaced.

**Air Filter Indicator Light**:

The filters have a useful life of one year in a typical residential environment.

* **Green** LED light is On – The filters have been in service for less than 6 months.
* **Orange** LED light is On – The filters have been in service for more than 5 months.
* **Red** LED light is On – The filter has been in service for at least 6 months. It is time to remove the front grill and vacuum off the top pre-filter to maintain maximum air flow. **The filter does not need to be removed.**

Replace the front grill and **press only the filter reset button** to reset timer for (6) more months. When both the “Air Filter” and “UV Lamp” LED service lights turn red at the same time, filters and UV Lamp have been in service for one year and need to be replaced.

**Ultraviolet Lamp Indicator Light**:

The UVC Germicidal Ultraviolet Lamp has a useful life of one year (9,000 hours) with a one-month grace period.

* **Green LED light is On** – The lamp has been in service for less than 12 months.
* **Orange** **LED light is On** – The lamp has been in service for more than 11 months. It’s time to order a new UVC Germicidal Ultraviolet Lamp and replacement filter.
* **Red** **LED light is On** – The lamp has been in service for more than 12 months. The UVC Germicidal Ultraviolet Lamp may not be effective and must be replaced

**Performing Maintenance**


Maintenance includes the following procedures:

* Replacing the ultraviolet UVC Germicidal Ultraviolet Lamp.
* Replacing the filters.

**Replacing the Germicidal Ultraviolet Lamp**

1. Unplug the Purifier’s power cord from the electrical outlet.
2. Using index fingers, squeeze the locking tabs (figure 6) inwards towards the center of the grill. Lift the grill up and remove.

!




**FIGURE**

**6**

1. Rotate the Ultraviolet Lamp one-quarter turn, top to rear, (figure 7) and remove lamp.

!



**FIGURE**

**7**

**FIGURE**

**7**

**a**

1. Insert the new Ultraviolet Lamp in place and install by rotating one-quarter turn (top-to-front).
2. Replace the top grill removed in previous step 2 by pressing it into position until it locks. The aluminum reflector must be positioned over the UVC Germicidal Ultraviolet Lamp, nearest the front of the unit (figure 7a).
3. Reset Ultraviolet Lamp timer by lightly pressing the related RESET button on the Service Panel (located directly beside the “UV Lamp” LED indicator) with a pin or similar object. The “UV Lamp” LED

service light will turn green, and the 6 month timer will reset. This completes UVC Germicidal Ultraviolet Lamp replacement procedures.



**Replacing the Filters:**

When both the “Air Filter” and “UV Lamp” LED Indicator lights turn **red**, both filters and UV lamp have been in service for one year and should be replaced within 30 days.

1. Unplug the Purifier’s power cord from the electrical outlet.

1. Rest the Purifier on its back (figure 8) to access the bottom of the unit.

! !



**FIGURE**

**8**

**FIGURE**

**9**

1. Press-up on locking clips at the bottom of the  front grill.



**FIGURE**

**10**

4.Lift bottom of grill upwards, and slide the grill out from the top of the unit. (figure 9)

5.Pull out the two filters individually and discard them.

6.Install new **white** HEPA filter (**labeled second  stage**) first, with its **white** layer facing upwards.  (figure 10 )

7.Install the new pre-filter (**labeled first stage**) in the remaining slot, with its **white** or **green** side facing upwards.

8.Replace grill. Slide upper end into grill slot and snap the bottom into place until it locks.

Reset the Filter Replacement timer by lightly pressing the RESET button on the Service Panel (located directly beside the “Air Filter” LED indicator) with a pin or similar object. The “Air Filter” LED light will turn **green** and the timer will be reset. This completes filter replacement procedures.

Restore the Purifier to normal operation as follows:

1. Set the unit in its normal operating position.
2. Plug the power cord into the wall outlet. Press the “Power” (ON/OFF) switch to operate.

.

|  |  |
| --- | --- |
|  | **SPECIFICATIONS** |
| **Model** | **Trio-1000P** |
| Dimensions | 21.5"wide X 18"high X 8" deep |
| Weight | 23lbs |
| Maximum Airflow | 265 cfm |
| Power Consumption | 106 watts, .89 amps |
| Voltage | 115v / 1ph / 60hz |
| Blower | Backward-curved motorized impeller - sealed bearings |
| UVC Germicidal Lamp | 10 watts |
| Microwatts at surface per cm2 | 16,000 |
| Microwatts at surface per cm2 @ 1ft | 540 |
| UVC Germicidal Wavelength | 254 nanometers |
| Stage 1 Pre-Filter | 5 micron |
| Stage 2 HEPA Filter | .30 micron hospital grade |
| Stage 1 Gas Absorption Layer | Activated Charcoal |
| Stage 2 Gas Absorption Layer | Activated Charcoal |
| Application Range | 1000 square feet (auto mode) |
| Service Interval | 1 Year lamp and filter replacement |
| Catalyst | TiO2 Anatase |
| Filter Efficiency % | 99% |
| Sound Level dBA | 48 to 68 |
| Agency Compliance | ETL, CSA |
| Warranty | 10 Year Limited Warranty excluding lamp and filters |

Limited Warranty

10 Year Limited Warranty

Refer to www.fieldcontrols.com for complete warranty statement.